## Bray Simple Set Max
QUICK - CALC Bray Simple Set Max Pressure Independent Control Valve
Setting & Selection Program
Enter your specified gallon per minute (gpm) flow in the yellow box and refer to the red column (D) for the required setting on your desired valve size.
Input
Eingabe dP = | 20 | (kPa) Differenzdruck am Ventil
Input Q = | 300 | (gpm) Flow |  | 68.1374
The following Covers ANSI125/150 & ANSI 250/300 Models
Dimension | Range |  | Calculation
| Flow (gpm) | Range ∆Pp(psi) | Pre-set | Min. ∆P (kPa) | Min. ∆P (psi)
DN50 Low Flow | 10,92 - 66,03 | 1,02 - 116,03 | NOT POSSIBLE | NOT POSSIBLE | NOT POSSIBLE
DN50 High Flow | 17,28 - 105,65 | 2,76 - 116,03 | NOT POSSIBLE | NOT POSSIBLE | NOT POSSIBLE
2.5" SSM-250-A-L | 19,27 - 110,06 | 2,18 - 116,03 | NOT POSSIBLE | NOT POSSIBLE | NOT POSSIBLE
2.5" SSM-250-A-H | 26,21 - 154,11 | 4,35 - 116,03 | NOT POSSIBLE | NOT POSSIBLE | NOT POSSIBLE
3" SSM-3-A-L | 25,53 - 149,78 | 2,32 - 116,03 | NOT POSSIBLE | NOT POSSIBLE | NOT POSSIBLE
3" SSM-3-A-H | 30,92 - 189,47 | 3,34 - 116,03 | NOT POSSIBLE | NOT POSSIBLE | NOT POSSIBLE
4" SSM-4-A-L | 46,23 - 308,20 | 2,90 - 116,03 | NOT POSSIBLE | NOT POSSIBLE | NOT POSSIBLE
4" SSM-4-A-H | 59,44 - 396,26 | 4,35 - 116,03 | 3.4261 | 53.4162 | 7.7474
5" SSM-5-A-L | 81,45 - 484,32 | 2,32 - 116,03 | 2.7162 | 19.8151 | 2.8739
5" SSM-5-A-H | 101,26 - 594,39 | 3,92 - 116,03 | 2.1027 | 29.2025 | 4.2355
6" SSM-6-A-L | 112,71 - 651,59 | 3,05 - 116,03 | 1.9263 | 21 | 3.0458
6" SSM-6-A-H | 140,89 - 858,56 | 4,79 - 116,03 | 1.4577 | 33 | 4.7863
8" SSM-8-A-L | 418,3 - 925,5 | 1,59 - 116,03 | NOT POSSIBLE | NOT POSSIBLE | NOT POSSIBLE
8" SSM-8-A-H | 572,4 - 1232,7 | 4,50 - 116,03 | NOT POSSIBLE | NOT POSSIBLE | NOT POSSIBLE
10" SSM-10-A-L | 836,6 - 2091,3 | 1,45 - 116,03 | NOT POSSIBLE | NOT POSSIBLE | NOT POSSIBLE
10" SSM-10-A-H | 1078,8 - 2641,7 | 2,18 - 116,03 | NOT POSSIBLE | NOT POSSIBLE | NOT POSSIBLE
12" SSM-12-A-L | 836,6 - 2091,3 | 1,45 - 116,03 | NOT POSSIBLE | NOT POSSIBLE | NOT POSSIBLE
12" SSM-12-A-H | 1078,8 - 2641,7 | 2,18 - 116,03 | NOT POSSIBLE | NOT POSSIBLE | NOT POSSIBLE
Range ∆Pp is defined from Min. Pump pressure (Min. ∆Pp) to Max. Pump pressure (Max.∆Pp) .
ACHTUNG !! BITTE HIER NICHT DATEN ÄNDERN
Type |  |  | X | Z |  | Kvs | Min | Max | Evaluering af Flow
DN50 Low Flow | [5 empty] | 33.5 | 2.48 | 15 | UDEN FOR OMRÅDET
DN50 High Flow | [5 empty] | 33.5 | 3.92 | 24 | UDEN FOR OMRÅDET
DN65 Low Flow | [5 empty] | 50 | 4.38 | 25 | UDEN FOR OMRÅDET
DN65 High Flow | [5 empty] | 50 | 5.95 | 35 | UDEN FOR OMRÅDET
DN80 Low Flow | [5 empty] | 68 | 5.3 | 34 | UDEN FOR OMRÅDET
DN80 High Flow | [5 empty] | 68 | 7 | 43 | UDEN FOR OMRÅDET
DN100 Low Flow | [5 empty] | 115 | 12.1 | 68 | UDEN FOR OMRÅDET
DN100 High Flow | [5 empty] | 115 | 14.8 | 90 | 68.1374
DN125 Low Flow | [5 empty] | 167 | 18.5 | 110 | 68.1374
DN125 High Flow | [5 empty] | 167 | 23 | 135 | 68.1374
DN150 Low Flow | [5 empty] | 250 | 25.6 | 148 | 68.1374
DN150 High Flow | [5 empty] | 241.9 | 32 | 195 | 68.1374
DN200 Low Flow | [5 empty] | 371 | 95 | 210 | UDEN FOR OMRÅDET
DN200 High Flow | [5 empty] | 317 | 130 | 280 | UDEN FOR OMRÅDET
DN250 Low Flow | [5 empty] | 840 | 190 | 475 | UDEN FOR OMRÅDET
DN250 High Flow | [5 empty] | 717 | 245 | 600 | UDEN FOR OMRÅDET
DN300 Low Flow | [5 empty] | 840 | 190 | 475 | UDEN FOR OMRÅDET
DN300 High Flow | [5 empty] | 717 | 245 | 600 | UDEN FOR OMRÅDET